## Read Me
Drinking Water and Wastewater Research Workbook
This workbook presents the team's findings from a comprehensive literature review to identify savings opportunities in drinking water pumping systems, wastewater pumping systems, and piping distribution systems. The workbook contains raw data inputs identified in the literature review and calculations to determine the savings opportunities presented in associated flyers.
Methodology
Literature Review: The team conducted an extensive literature review encompassing research on energy, water, cost, and carbon savings opportunities associated with pumps and plastic pipes. The review included life cycle analysis reports, academic papers, industry white papers, and water system infrastructure statistics. The red tabs hold all research findings.
Savings Opportunity Calculations: Subsequently, the team performed calculations to quantify the potential savings. For pumps, this included determining energy, cost, and carbon savings achieved through the adoption of variable frequency drives and more efficient pumps. For pipes, this involved determining savings from "cradle-to-installation opportunities" (manufacturing and installation savings and benefits) and "operational opportuniites" (reduced burst failures, background leakage, and frictional losses). All piping savings and benefits are compared relative to metal piping alternatives. The blue tabls hold details on all calculations.
Expert Validation: The team consulted subject matter experts from the municipal water and wastewater industry as well as the plastic piping industry and incorporated their input into the findings. This helped ensure the findings, based on exisiting literature, were representative of specialists' experience in the field.
Research Findings Summary: The green 'Research Findings' tab presents the results from this investigation and calculations.
Tab Name | Description
Research Findings | This tab summarizes the information included in the Drinking Water and Wastewater Savings Opportunity designed deliverables (available *******).
Calc -Pump Energy Consumption | This tab contains the calculations used to estimate the energy use of wastewater and water treatment pumps. It also presents data used to compare and corroborate those values.
Calc - Pump Energy Savings Mechanisms | This tab holds the calculations to estimate savings associated with different energy efficiency opportunities for wastewater and water treatment systems.
Calc - Piping | This tab contains the calculations used to estimate the energy, cost, carbon and water savings from plastic piping.
Research - Pumps | This tab holds information informing the calculations on the 'Pump Energy Consumption' and 'Pump Energy Savings Mechanisms' tabs, as well as a description of assumptions used in the calculations.
Research - Pipes | This tab holds information informing the calculations on the 'Piping Calculations' tab, as well as a description of assumptions used in the calculations.
Research - Water Infrastructure | This tab holds information informing the calculations on the 'Pump Energy Consumption', 'Pump Energy Savings Mechanisms', and 'Piping Calculations' tab, as well as a description of assumptions used in the calculations.
Stats | This tab summarizes the constants, conversion factors, and water and wastewater infrastructure statistics used in the research.
Note on D12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Where will these be available. HI, ACC, and VI websites?

## Research Findings
Summary of Research Findings
This tab summarizes the information that will be included in the Water and Wastewater Savings Opportunity designed deliverables.
Drinking Water Pumping Opportunities
Various types of pumps are used in drinking water systems, including centrifugal pumps, submersible pumps, or vertical turbine pumps. These pumps are designed to move water efficiently and can handle large volumes of water.
# of Water Treatment Plants in the United States
| Value | Units
| 148000 | Water Treatment Plants
ASCE Drinking Water Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2017/01/Drinking-Water-2021.pdf
Annual Drinking Water Consumed in the United States
| Value | Units
| 14235 | Billion gallons
ASCE Drinking Water Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2017/01/Drinking-Water-2021.pdf
National Drinking Water Pumping Energy Consumption
| Value | Units
| 35348.8995 | GWh | 3323826.9386 | American homes
Cadeo calculated nation-wide pumping energy consumption based on scaling values found in EPRI's Electricity Use and Management in the Municipal Water Supply and Wastewater Industries, (https://www.epri.com/research/products/000000003002001433) to the year 2022.
Drinking Water Pumping Consumption, by application
| Applications | % of Pumping Electricity Consumption
| Distribution Pumping | 67%
| In-Plant Water Pumping | 8%
| Water Intake Pumping | 11%
| Water Treatment | 14%
Quantifying Energy Use in the U.S. Public Water Industry - A Summary, https://www.hansenallenluce.com/wp-content/uploads/2015/11/Energy-Use-Water-Sector.pdf
`
Savings Opportunity for Right-Sizing Drinking Water Pumps using VFDs
| Value |  | Units
| Energy savings per year | 1972.5034 | GWh | 185472.8144 | American homes
| Cost savings per year | 166676535.7041 | $
| Carbon savings per year | 769276.3186 | metric tons CO2 | 171548.6191 | Gas power cars avoided annually
Cadeo calculated nation-wide potential based on DOE's 2021 Motor System Market Assessment, BPA's ASD Market Model, and feedback from subject matter experts
Savings Opportunity for Load Matching Drinking Water Pumps using VFDs
| Value |  | Units
| Energy savings per year | 2498.0152 | GWh | 234886.2407 | American homes
| Cost savings per year | 211082281.8946 | $
| Carbon savings per year | 974225.9164 | metric tons CO2 | 217252.3794 | Gas power cars avoided annually
Cadeo calculated nation-wide potential based on DOE's 2021 Motor System Market Assessment, BPA's ASD Market Model, and feedback from subject matter experts
Combined Savings Opportunity for Drinking Water Pumps using VFDs
| Value |  | Units
| Energy savings per year | 4470.5186 | GWh | 420359.0551 | American homes
| Cost savings per year | 377758817.5987 | $
| Carbon savings per year | 1743502.2351 | metric tons CO2 | 388800.9984 | Gas power cars avoided annually
Cadeo calculated nation-wide potential based on DOE's 2021 Motor System Market Assessment, BPA's ASD Market Model, and feedback from subject matter experts
Savings Opportunity for Replacing Existing Pumps with more Efficient Pumps
| Value |  | Units
| Energy savings per year | 507.7556 | GWh | 47743.8228 | American homes
| Cost savings per year | 42905344.4576 | $
| Carbon savings per year | 198024.6667 | metric tons CO2 | 44159.5007 | Gas power cars avoided annually
Cadeo calculated nation-wide potential based on DOE's 2021 Motor System Market Assessment, BPA's ASD Market Model, and feedback from subject matter experts
Combined Savings Opportunity for an Optimized Drinking Water pumping system
| Value |  | Units
| Energy savings per year | 4978.2741 | GWh | 468102.878 | American homes
| Cost savings per year | 420664162.0563 | $
| Carbon savings per year | 1941526.9018 | metric tons CO2 | 432960.4991 | Gas power cars avoided annually
Cadeo calculated nation-wide potential based on DOE's 2021 Motor System Market Assessment, BPA's ASD Market Model, and feedback from subject matter experts
Wastewater Treatment Pumping Opportunities
Various types of pumps are used in wastewater systems, including centrifugal pumps, submersible pumps, or vertical turbine pumps. These pumps are designed to move water efficiently and can handle large volumes of water.
# of Wastewater Treatment Plants in the United States
| Value | Units
| 16000 | Wastewater Treatment Plants
ASCE Wastewater Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2020/12/Wastewater-2021.pdf
Annual Wastewater Processed in the United States
| Value | Units
| 22812.5 | Billion gallons
ASCE Wastewater Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2020/12/Wastewater-2021.pdf
National Wastewater Pumping Energy Consumption
| Value | Units
| 21250.3416 | GWh | 1998151.538 | American homes
Cadeo calculated nation-wide pumping energy consumption based on scaling values from DOE's 2018 Motor System Market Assessment (https://motors.lbl.gov/) to 2022
Wastewater Motor-Driven Electricity Consumption, by Equipment Type.
| Equipment | Wastewater System Motor-Driven Electricity Consumption (%)
| Pump | 62.22%
| Air Compressor | 8.316%
| Fan and Blower | 17.45%
| Material Processing | 10.83%
| Other | 1.186%
| TOTAL | 100%
Rao, P., Sheaffer, P., Chen, Y., Goldberg, M., Jones, B., Cropp, J., and J. Hester. U.S. Industrial and Commercial Motor System Market Assessment Report Volume 1: Characteristics of the Installed Base. Lawrence Berkeley National Laboratory, January 2021, https://eta.lbl.gov/publications/us-industrial-and-commercial-motor
Savings Opportunity for Right-Sizing Wastewater Pumps using VFDs
| Value |  | Units
| Energy savings per year | 1417.079 | GWh | 133246.7346 | American homes
| Cost savings per year | 119743177.4227 | $
| Carbon savings per year | 552660.8189 | metric tons CO2 | 123243.3626 | Gas power cars avoided annually
Cadeo calculated nation-wide potential based on EPRI's Electricity Use and Management in the Municipal Water Supply and Wastewater Industries report, BPA's ASD Market Model, and feedback from subject matter experts
Savings Opportunity for Load Matching Wastewater Pumps using VFDs
| Value |  | Units
| Energy savings per year | 2928.3457 | GWh | 275349.8581 | American homes
| Cost savings per year | 247445215.1193 | $
| Carbon savings per year | 1142054.839 | metric tons CO2 | 254678.2291 | Gas power cars avoided annually
Cadeo calculated nation-wide potential based on EPRI's Electricity Use and Management in the Municipal Water Supply and Wastewater Industries report, BPA's ASD Market Model, and feedback from subject matter experts
Combined Savings Opportunity for Wastewater Pumps using VFDs
| Value |  | Units
| Energy savings per year | 4345.4248 | GWh | 408596.5927 | American homes
| Cost savings per year | 367188392.542 | $
| Carbon savings per year | 1694715.6579 | metric tons CO2 | 377921.5917 | Gas power cars avoided annually
Cadeo calculated nation-wide potential based on EPRI's Electricity Use and Management in the Municipal Water Supply and Wastewater Industries report, BPA's ASD Market Model, and feedback from subject matter experts
Savings Opportunity for Replacing Existing Wastewater Pumps with More Efficient Pumps
| Value |  | Units
| Energy savings per year | 305.2423 | GWh | 28701.6727 | American homes
| Cost savings per year | 25792973.4608 | $
| Carbon savings per year | 119044.4929 | metric tons CO2 | 26546.9219 | Gas power cars avoided annually
Cadeo calculated nation-wide potential based on EPRI's Electricity Use and Management in the Municipal Water Supply and Wastewater Industries report, BPA's ASD Market Model, and feedback from subject matter experts
Combined Savings Opportunity for an Optimized Wastewater Pumping System
| Value |  | Units
| Energy savings per year | 4650.6671 | GWh | 437298.2655 | American homes
| Cost savings per year | 392981366.0027 | $
| Carbon savings per year | 1813760.1508 | metric tons CO2 | 404468.5136 | Gas power cars avoided annually
Cadeo calculated nation-wide potential based on EPRI's Electricity Use and Management in the Municipal Water Supply and Wastewater Industries report, BPA's ASD Market Model, and feedback from subject matter experts
Piping Opportunities
Drinking Water System Stats
| Value |  | Units
| Nationwide length of installed water mains | 2.2 | million mi | Utah State University, https://digitalcommons.usu.edu/cgi/viewcontent.cgi?article=1173&context=mae_facpub
| Estimated water mains to be replaced annually | 12000 | miles | ASCE Drinking Water Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2017/01/Drinking-Water-2021.pdf
Wastewater System Stats
| Value |  | Units
| Nationwide length of wastewater pipes | 0.8 | million mi | ASCE Wastewater Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2020/12/Wastewater-2021.pdf
| Estimated wastewater pipes replaced annually | 4700 | miles | ASCE Wastewater Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2020/12/Wastewater-2021.pdf
Annual water/energy/cost/carbon savings due to reduced pipe failures if all drinking water pipes were plastic
| Value |  | Units
| Water savings per year | 58103.1792 | Million gallons
| Energy savings per year | 81.9255 | GWh | 7703.3834 | American homes
| Cost savings per year | 615970703.2858 | $
| Carbon savings per year | 31950.9382 | Metric tons CO2 | 7125.0592 | Gas power cars avoided annually
Any numbers presented on these infographics without a direct footnote are the result of Cadeo research and analysis based on publicly available data and reports.
Annual water/energy/cost/carbon savings due to reduced pipe leaks if all drinking water pipes were plastic
| Value |  | Units
| Water savings per year | 1423500 | Billion gallons
| Energy savings per year | 2007.135 | GWh | 188729.1961 | American homes
| Cost savings per year | 169602907.5 | $
| Carbon savings per year | 782782.65 | Metric tons CO2 | 174560.531 | Gas power cars avoided annually
Any numbers presented on these infographics without a direct footnote are the result of Cadeo research and analysis based on publicly available data and reports.
Annual energy/cost/carbon savings due to reduced frictional losses if all drinking water pipes were plastic
| Value |  | Units
| Energy savings per year | 7278.5856 | GWh | 684399.2102 | American homes
| Cost savings per year | 615040483.2 | $
| Carbon savings per year | 2838648.384 | Metric tons CO2 | 633018.5896 | Gas power cars avoided annually
Any numbers presented on these infographics without a direct footnote are the result of Cadeo research and analysis based on publicly available data and reports.
Combined annual operational savings if all drinking water pipes were plastic
| Value |  | Units
| Water savings per year | 1481603.1792 | Million gallons
| Energy savings per year | 9367.6461 | GWh | 880831.7896 | American homes
| Cost savings per year | 1400614093.9858 | $
| Carbon savings per year | 3653381.9722 | Metric tons CO2 | 814704.1798 | Gas power cars avoided annually
Any numbers presented on these infographics without a direct footnote are the result of Cadeo research and analysis based on publicly available data and reports.
Cradle-to-installation savings
Cost and carbon reductions from using plastic pipe compared to ductile iron pipe
Value
| Cost savings* | 20-40%
| Carbon savings** | 30-50%
These are the range of values identified from various LCA reports reviewed. Values depend on plastic type material and characteristics of pipes
*https://www.jmeagle.com/pvc-vs-ductile-iron-pipe-installed-cost-comparison-calculator
*https://pvc4pipes.com/wp-content/uploads/2019/06/PVC-U_pipe_competitiveness_TCO_Althesys-fact-sheet_final.pdf
**Life Cycle Analysis for Water and Wastewater Pipe Materials, Fei Du, S.M.ASCE; Gwendolyn J. Woods, S.M.ASCE; Doosun Kang; Kevin E. Lansey, A.M.ASCE; and Robert G. Arnold, M.ASCE
**Climate Impact of Plastics, https://www.mckinsey.com/~/media/mckinsey/industries/chemicals/our%20insights/climate%20impact%20of%20plastics/climate-impact-of-plastics_vf.pdf
Combined Plastic and Piping Savings Opportunities
| Value |  | Units
| Water savings per year | 1481603.1792 | Million gallons
| Energy savings per year | 18996.5872 | GWh | 1786232.9331 | American homes
| Cost savings per year | 2214259622.0448 | $
| Carbon savings per year | 7408669.0248 | Metric tons CO2 | 1652133.1925 | Gas power cars avoided annually

## Calc - Pump Energy Consumption
Pump Energy Consumption
This analysis uses a top-down approach to calculate savings associated with different pump efficiency options for water treatment and wastewater systems.
To calculate savings, the team first estimated the energy consumed by pumps in water treatment and wastewater systems. This tab presents the data sources used to estimate pump energy consumption, and provides comparison points to help conceptualize the magnitude of the values.
Value |  | Units
National Wastewater Pumping | 21250.3416 | GWh
National Water Treatment Pumping | 35348.8995 | GWh
Wastewater Energy Consumption
https://motors.lbl.gov/
DOE's motor system market assessment included wastewater as an industrial subsector in its assessment. This data is representative of the 2018 motor stock, and also includes the energy consumed by each motor-drive equipment for each industrial subsector.
To estimate the 2022 pump electricity use, the team scaled the MSMA's estimate of pump electricity use from 2018 to 2022 using the national gross output attributed to of state and local government.
Wastewater System Electricity Consumption Distribution
Equipment | Wastewater System Motor-Driven Electricity Consumption (GWh) | Wastewater System Motor-Driven Electricity Consumption (%)
Air Compressor | 2320 | 8.316%
Fan and Blower | 4868 | 17.45%
Material Handling | 74 | 0.2653%
Material Processing | 3022 | 10.83%
Other | - | -
Pump | 17357 | 62.22%
Refrigeration Compressor | Q | Q
UTC | Q | Q
TOTAL | 27898 | 100%
Q = Due to the low number of facilities/systems matching the selected criteria, the results are statistically insignificant UTC = Unable to collect specific data, "-" = No matching motor data
Direct link to this specific set of results: https://motors.lbl.gov/analyze/7-0b2G
Wastewater System Pumping Electricity Consumption
Year | Electricity Consumption | Units
2018 | 17357 | GWh
2022 | 21250.3416 | GWh
Direct link to this specific set of results: https://motors.lbl.gov/analyze/7-0b2G
Gross Output, State and Local Government, by year (Billions dollars)
| 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022
State and Local Government | 2538.8 | 2618.7 | 2752 | 2862.6 | 2847 | 3058.7 | 3369.3
General government | 2204.9 | 2274.3 | 2386.8 | 2487.3 | 2512.6 | 2680 | 2939
Government enterprises | 333.9 | 344.4 | 365.2 | 375.3 | 334.4 | 378.7 | 430.3
https://www.bea.gov/itable/gdp-by-industry
Comparison
The team compared the calculated value to the pump energy use presented in the Northwest Power and Conservation Council's 2021 Power Plan for the Wastewater industry in the Pacific Northwest. The team scaled the 2018 MSMA value to represent the Pacific Northwest using the estimate that Washington, Oregon, Idaho, and Western Montana make up approximately 3.5% of the national population. The team also scaled the 2018 MSMA value to represent 2016 using Gross Output of state and local government, as that is the year presented in the 2021 Power Plan documentation.
The 2021 Plan estimate is approximately 20% different than the MSMA value, corroborating the relative size of the energy consumption estimate.
Source | Value | Unit
2021 Plan (2016) | 438000 | MWh
2018 MSMA, scaled to 2016 and the PNW | 560431.7972 | MWh
https://nwcouncil.app.box.com/s/u0dgjxkoxoj2tttym81uka3wrjcy6bo6/file/655808922371
EPRI: Electricity Use and Management in the Municipal Water Supply and Wastewater Industries
https://www.epri.com/research/products/000000003002001433
To calculate the energy use of pumps in water treatment, the team used information from the Electric Power Research Institute (EPRI) and national electricity use from the US Energy Information Administration (EIA). This calculation assumes that the percent of national electricity used by Water Treatment is constant year-to-year.
Value |  | Units
Annual Water Treatment Energy Use, 2011 | 39200000000 | kWh
Percent of Water Treatment and Supply electricity used by pumps** | 86%
Information | Electricity (billion kWh) | Link | Table | AEO version
National Electricity Use, 2011 | 3895.3625 | https://www.eia.gov/outlooks/aeo/data/browser/#/?id=8-AEO2012&sourcekey=0 | Electricity Supply, Disposition, Prices, and Emissions | AEO 2012
National Electricity Use, 2022 | 4084.5034 | https://www.eia.gov/outlooks/aeo/data/browser/#/?id=8-AEO2023&region=0-0&cases=ref2023&start=2021&end=2050&f=A&linechart=ref2023-d020623a.6-8-AEO2023~ref2023-d020623a.56-8-AEO2023&ctype=linechart&sid=ref2023-d020623a.56-8-AEO2023&sourcekey=0 | Table 8 | AEO, 2023
Sector | Energy Consumption | Units
Water Treatment and Supply Pumping Energy Use, 2022 | 35348899491.5159 | kWh
Comparison
Other sources estimated energy use of pump water systems at 33.0 billion kWh in 2009, very close to the 2011 value used in this calculation.
Source: Sanders, Kelly & Webber, Michael. (2011). Evaluating the Energy Intensity of the US Public Water System. ASME 2011 5th International Conference on Energy Sustainability, ES 2011. 10.1115/ES2011-54165.

## Calc - Pump Energy Savings
Pump Energy Savings Mechanisms
This tab presents the energy savings estimates for three efficiency opportunities: right-sizing pumping equipment, load-matching with variable speed control, and upgrades to efficient pumps.
Right Sizing
The team used their equation to calculate the savings associated with right-sizing, specific to the wastewater and drinking water systems.
Where
Electricity Consumption = | Total segment pumping electricity consumption
%Rotodynamic = | The percent of pump energy use that is consumed by rotodynamic pumps
%PumpingEnergyLF = | % of pumping energy used by pumps at the specific load factor
ηVFD = | Average VFD efficiency
LF = | Load Factor
x = | Practical Relationship for affinity laws, 2.1
%NoControl = | Percent of pump energy consumption that is not already controlled (i.e., efficiently right-sized
The team assumed that right sizing, as a savings opportunity, applies only to constant load systems (as the "load matching" savings opportunity, described in another tab, applies to the variable load systems). The equation above uses "1-%Rotodynamic" as equivalent to %PositiveDisplacement, or the percent of pump energy consumed by positive displacement pumps.
Wastewater
Wastewater Electricity Consumption |  | 21250.3416 | GWh
%NoControl |  | 85.78%
| ηvfd | 94.94%
| %Rotodynamic | 85%
Segment | Load Factor | Percent of Wastewater Pumping Energy Consumption* |  | Energy Saving, GWh
Wastewater | 0.4 | 0% |  | 0
| 0.75 | 3.822% |  | 279.7377
| 0.9 | 35.77% |  | 1137.3413
Total |  |  |  | 1417.079
Savings Values | Value | Units
Electricity | 1417.079 | GWh
Dollars | 119743177.4227 | $
Carbon | 552660.8189 | metric tons CO2
Water Treatment
Water Treatment Pumping Electricity Consumption |  | 35348.8995 | GWh
%NoControl |  | 50%
| ηvfd | 94.94%
| %Rotodynamic | 90%
Segment | Load Factor | Percent of Wastewater Pumping Energy Consumption* |  | Energy Saving, GWh
Wastewater | 0.4 | 0% |  | 0
| 0.75 | 9.5% |  | 690.4523
| 0.9 | 40.5% |  | 1282.0511
Total |  |  |  | 1972.5034 | GWh
Savings Values | Value | Units
Electricity | 1972.5034 | GWh
Dollars | 166676535.7041 | $
Carbon | 769276.3186 | metric tons CO2
Load Matching
Where
Electricity Consumption = | Total segment pumping electricity consumption
%NoControl = | Percent of pump energy consumption that is not already controlled (i.e., already has an ASD)
%PumpingEnergyLF = | % of pumping energy used by pumps at the specific load factor
ηVFD = | Average VFD efficiency
%Rotodynamic = | The percent of pump energy use that is consumed by rotodynamic pumps
LPFNC = | Load Profile Factor for pumps with No Control
LPFVFD = | Load Profile Factor for pumps with VFDs
This calculation assumes that the load matching savings from VFDs are only applicable to rotodynamic pumps, as they are variable torque systems that see large power savings from decreases in motor speed
Wastewater
Wastewater Electricity Consumption |  | 21250.3416
%NoControl |  | 85.78%
%Rotodynamic |  | 85%
| ηvfd | 94.94%
Load Type | Load Factor | Percent of Wastewater Pumping Energy Consumption* |  | Load Profile Factor, No Control | Load Profile Factor, VFD | Energy Saving, GWh
Variable Load | 0.4 | 5.835% |  | 0.76662 | 0.22103 | 610.9434
| 0.75 | 45.97% |  | 0.90884 | 0.6172 | 2169.9691
| 0.9 | 8.607% |  | 0.96374 | 0.85152 | 147.4333
Total | [5 empty] | 2928.3457 | GWh
Savings Values | Value | Units
Electricity | 2928.3457 | GWh
Dollars | 247445215.1193 | $
Carbon | 1142054.839 | metric tons CO2
Water Treatment
Water Treatment Electricity Consumption |  | 35348.8995
%NoControl |  | 50%
%Rotodynamic |  | 90%
| ηvfd | 94.94%
Segment | Load Factor | Percent of Water Treatment Pumping Energy Consumption* |  | Load Profile Factor, No Control | Load Profile Factor, VFD | Energy Saving, GWh
Variable Load | 0.4 | 6.5% |  | 0.76662 | 0.22103 | 698.6518
| 0.75 | 33.5% |  | 0.90884 | 0.6172 | 1623.5048
| 0.9 | 10% |  | 0.96374 | 0.85152 | 175.8586
Total | [5 empty] | 2498.0152 | GWh
Savings Values | Value | Units
Electricity | 2498.0152 | GWh
Dollars | 211082281.8946 | $
Carbon | 974225.9164 | metric tons CO2
Efficient Pumps
Where
Electricity Consumption = | Total segment pumping electricity consumption
%Energy200HPSmaller = | The percent of pumping energy that is attributed to pumps 200HP or smaller
ΔPumpEfficiency200HPSmaller = | Average increase in pump efficiency between a standard and more efficient pump that is 200HP or smaller
%EnergyGreater200HP = | The percent of pumping energy that is attributed to pumps larger than 200HP
ΔPumpEfficiencyGreater200HP = | Average increase in pump efficiency between a standard and more efficient pump that is larger than 200HP
This calculation assumes the efficiency increase is applicable to both rotodynamic and positive displacement pumps.
Wastewater
Wastewater Electricity Consumption |  | 21250.3416
%200HP or Smaller |  | 26.75%
%Greater than 200 HP |  | 73.25%
ΔPumpEfficiency200HPSmaller |  | 4%
ΔPumpEfficiencyGreater200HP |  | 0.5%
Wastewater Electricity Savings, Pump Efficiency |  | 305.2423
Savings Values | Value | Units
Electricity | 305.2423 | GWh
Dollars | 25792973.4608 | $
Carbon | 119044.4929 | metric tons CO2
Water Treatment
Water Treatment Electricity Consumption |  | 35348.8995
%200HP or Smaller |  | 26.75%
%Greater than 200 HP |  | 73.25%
ΔPumpEfficiency200HPSmaller |  | 4%
ΔPumpEfficiencyGreater200HP |  | 0.5%
Water Treatment Electricity Savings, Pump Efficiency |  | 507.7556
Savings Values | Value | Units
Electricity | 507.7556 | GWh
Dollars | 42905344.4576 | $
Carbon | 198024.6667 | metric tons CO2
𝐸𝑛𝑒𝑟𝑔𝑦 𝑆𝑎𝑣𝑖𝑛𝑔𝑠=(𝐸𝑙𝑒𝑐𝑡𝑟𝑖𝑐𝑖𝑡𝑦 𝑐𝑜𝑛𝑠𝑢𝑚𝑝𝑡𝑖𝑜𝑛 ×%𝑅𝑜𝑡𝑜𝑑𝑦𝑛𝑎𝑚𝑖𝑐 ×%𝑃𝑢𝑚𝑝𝑖𝑛𝑔𝐸𝑛𝑒𝑟𝑔𝑦_𝐿𝐹×𝜂_𝑉𝐹𝐷× (1−𝐿𝐹^𝑥 )×%𝑁𝑜𝐶𝑜𝑛𝑡𝑟𝑜𝑙)+
(𝐸𝑙𝑒𝑐𝑡𝑟𝑖𝑐𝑖𝑡𝑦 𝑐𝑜𝑛𝑠𝑢𝑚𝑝𝑡𝑖𝑜𝑛 ×(1−%𝑅𝑜𝑡𝑜𝑑𝑦𝑛𝑎𝑚𝑖𝑐 ) ×%𝑃𝑢𝑚𝑝𝑖𝑛𝑔𝐸𝑛𝑒𝑟𝑔𝑦_𝐿𝐹×𝜂_𝑉𝐹𝐷× (1−𝐿𝐹)×%𝑁𝑜𝐶𝑜𝑛𝑡𝑟𝑜𝑙)
𝐸𝑛𝑒𝑟𝑔𝑦 𝑆𝑎𝑣𝑖𝑛𝑔𝑠= (𝐸𝑙𝑒𝑐𝑡𝑟𝑖𝑐𝑖𝑡𝑦 𝑐𝑜𝑛𝑠𝑢𝑚𝑝𝑡𝑖𝑜𝑛 ×%𝑁𝑜𝐶𝑜𝑛𝑡𝑟𝑜𝑙×%𝑃𝑢𝑚𝑝𝑖𝑛𝑔𝐸𝑛𝑒𝑟𝑔𝑦_𝐿𝐹 ×𝜂_𝑉𝐹𝐷×%"Rotodynamic" )/(𝐿𝑃𝐹_𝑁𝐶 )∗(𝐿𝑃𝐹_𝑁𝐶 "−" 𝐿𝑃𝐹_𝑉𝐹𝐷 )
𝐸𝑛𝑒𝑟𝑔𝑦 𝑆𝑎𝑣𝑖𝑛𝑔𝑠=(𝐸𝑙𝑒𝑐𝑡𝑟𝑖𝑐𝑖𝑡𝑦 𝑐𝑜𝑛𝑠𝑢𝑚𝑝𝑡𝑖𝑜𝑛 ×%𝐸𝑛𝑒𝑟𝑔𝑦_200𝐻𝑃𝑆𝑚𝑎𝑙𝑙𝑒𝑟× 𝛥𝑃𝑢𝑚𝑝𝐸𝑓𝑓𝑖𝑐𝑖𝑒𝑛𝑐𝑦_200𝐻𝑃𝑆𝑚𝑎𝑙𝑙𝑒𝑟 )+
(𝐸𝑙𝑒𝑐𝑡𝑟𝑖𝑐𝑖𝑡𝑦 𝑐𝑜𝑛𝑠𝑢𝑚𝑝𝑡𝑖𝑜𝑛 ×%𝐸𝑛𝑒𝑟𝑔𝑦_𝐺𝑟𝑒𝑎𝑡𝑒𝑟200𝐻𝑃 × 𝛥𝑃𝑢𝑚𝑝𝐸𝑓𝑓𝑖𝑐𝑖𝑒𝑛𝑐𝑦_𝐺𝑟𝑒𝑎𝑡𝑒𝑟200𝐻𝑃)

## Calc - Piping
Plastic Piping Calculations
This tab include all calculations used to determine the savings opportunities for plastic pipes. Details on calculation inputs are found on the 'piping research' tab.
= Data inputs the team identified as having uncertainty and were vetted with SMEs
Constants Information
| Information | Value | Units
| National Electricity Cost (2022) | 0.0845 | $ per kWh (2022) | https://www.eia.gov/outlooks/steo/data/browser/#/?v=19
| National Water Cost (2022)* | 0.009863 | $ per gallon | https://www.circleofblue.org/2010/world/the-price-of-water-a-comparison-of-water-rates-usage-in-30-u-s-cities/
| Carbon Intensity | 0.00039 | metric tons per kWh | https://www.eia.gov/environment/emissions/carbon/#:~:text=Between%202005%20and%202021%2C%20the,to%200.39%20mt%20per%20megawatthour
*Assuming 30$/month @ 100 gal/day,
| Drinking Water Infrastructure Information | Value | Units
| Nationwide length of installed water mains | 2.2 | million mi | ASCE Drinking Water Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2017/01/Drinking-Water-2021.pdf
| Estimated water mains to be replaced in 2020 | 12000 | miles | ASCE Drinking Water Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2017/01/Drinking-Water-2021.pdf
| Nationwide consumption of drinking water | 14235 | billion gal | National Environmental Education Foundation, https://www.neefusa.org/story/water/home-water-use-united-states
| Avoided kWh per million gallons of water | 1410 | kWh/million gal | Sustainable Solutions Corporation, https://www.sustainablesolutionscorporation.com/resources
| Avoided CO2 per million gallons of water | 0.5499 | metric tons CO2/ million gal | Calculation
Drinking Water Pipe Material Distribution
| Pipe Material | % Distribution | Total length (million mi)
| AC | 13% | 0.286
| CI | 28% | 0.616
| CSC | 3% | 0.066
| DI | 28% | 0.616
| PVC | 22% | 0.484
| Steel | 3% | 0.066
| Other | 3% | 0.066
Utah State University, https://digitalcommons.usu.edu/cgi/viewcontent.cgi?article=1173&context=mae_facpub
| Wastewater Infrastructure Information | Value | Units
| Nationwide length of wastewater pipes | 0.8 | million mi | ASCE Wastewater Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2020/12/Wastewater-2021.pdf
| Estimated wastewater pipes replaced in 2019 | 4700 | miles | ASCE Wastewater Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2020/12/Wastewater-2021.pdf
| Wastewater processed per year | 22812.5 | billion gal | ASCE Wastewater Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2020/12/Wastewater-2021.pdf
Wastewater Pipe Material Distribution
| Pipe Material | % Distribution | Total length (million mi)
| Ductile Iron |  | 0
| Concrete |  | 0
| Vitrified Clay |  | 0
| PVC |  | 0
| HDPE |  | 0
Pipe Material Life Cycle Analysis (LCA) - Embodied Carbon
Source 1: Life Cycle GHG Emission Impact of 12" PVC Pipe per mi
| Pipe materials (12-in pipe) | Total GWP (10^3 kg CO2/mi) | Production | Installation | Transportation | Units
| PVC | 511.7716 | 506.9435 | 4.5223 | 0.41843 | Metric tons CO2/mi |  |  | 1 km = X miles conversion factor
| Ductile Iron | 759.6106 | 753.1732 | 5.2786 | 1.4162 | Metric tons CO2/mi |  |  | 0.62137
| Concrete | 109.9182 | 101.5496 | 4.6832 | 3.6371 | Metric tons CO2/mi
| HDPE | 350.8371 | 346.0091 | 4.5223 | 0.27359 | Metric tons CO2/mi
| Reinforced Concrete | 244.6204 | 234.9643 | 4.6832 | 3.9751 | Metric tons CO2/mi
| Cast Iron | 568.0986 | 561.6612 | 5.2786 | 1.3518 | Metric tons CO2/mi
Life Cycle Analysis for Water and Wastewater Pipe Materials, Fei Du, S.M.ASCE; Gwendolyn J. Woods, S.M.ASCE; Doosun Kang; Kevin E. Lansey, A.M.ASCE; and Robert G. Arnold, M.ASCE
| Source 2: Life Cycle GHG Emission Impact of 8" PVC Pipe per mi |  |  |  | 0.32627
| Life Cycle Stage | PVC - 8" DR25 PC165 C900 | PVC - 8" PS46 SDR35 D3034 Solid Wall | Units
| Raw Materials | 35.904 | 21.12 | Metric tons CO2/mi |  | 100 ft = X miles conversion factor
| Raw Material Transportation | 0.4752 | 0.4224 | Metric tons CO2/mi |  | 0.018939
| Pipe Manufacturing | 4.0656 | 3.8544 | Metric tons CO2/mi
| Packaging | 0.1056 | 0.1056 | Metric tons CO2/mi |  | 1 kg CO2 = X metric tons CO2 conversion factor
| Final Product Transportation | 0.792 | 0.4224 | Metric tons CO2/mi |  | 0.001
| Installation | 9.3984 | 13.2 | Metric tons CO2/mi
| Total | 50.688 | 39.072 | Metric tons CO2/mi
Sustainable Solutions Corporation, Life Cycle Assessment of PVC Water and Sewer Pipe and Comparative Sustainability Analysis of Pipe Materials
Plastic Pipe GHG Emission Impacts Relative to Ductile Iron
| PVC - % lower that DI (based on Fei Du Et al. LCA) | 32.63% | Life Cycle Analysis for Water and Wastewater Pipe Materials, Fei Du, S.M.ASCE; Gwendolyn J. Woods, S.M.ASCE; Doosun Kang; Kevin E. Lansey, A.M.ASCE; and Robert G. Arnold, M.ASCE
| HDPE - % lower that DI (based on Fei Du Et al. LCA) | 53.81% | Life Cycle Analysis for Water and Wastewater Pipe Materials, Fei Du, S.M.ASCE; Gwendolyn J. Woods, S.M.ASCE; Doosun Kang; Kevin E. Lansey, A.M.ASCE; and Robert G. Arnold, M.ASCE
| PVC - % lower that DI (based on McKinsey Report) | 35-40% | Climate Impact of Plastics, https://www.mckinsey.com/~/media/mckinsey/industries/chemicals/our%20insights/climate%20impact%20of%20plastics/climate-impact-of-plastics_vf.pdf
Pipe Material Life Cycle Cost (LCC) Data - Costs
`` | Source 1: Cost for 8" pipes per mile
| Life Cycle Costs | PVC | DI |  | 1 ft = X Miles conversion factor
| Material Cost | 33264 | 97067.52 |  | 0.00018939
| Labor & Equipment Cost | 30243.84 | 34780.416
| Backfill Cost | 30801.8078 | 30801.8078
| Source: https://www.jmeagle.com/pvc-vs-ductile-iron-pipe-installed-cost-comparison-calculator |  |  |  | 1 m = X Miles conversion factor
0.00062137
| % cost savings | 42.02%
Source 2: Cost for 12" pipes per mile
| Life Cycle Costs | Purchase | Installation |  | 1 € = X $ conversion factor
| PVC | 53011.8078 | 160078.2785 |  | 1.08
| DI | 97506.9644 | 173983.015
https://pvc4pipes.com/wp-content/uploads/2019/06/PVC-U_pipe_competitiveness_TCO_Althesys-fact-sheet_final.pdf
| % cost savings | 21.51%
Drinking Water Pipe Failure and Leakage Calculations
Burst Failures
| Stat | Value | Unit
| Average cost to repair a water main break | 2400 | $ | City of Milwaukee, https://city.milwaukee.gov/water/customer/WatermainsReplacementandMaintenance.htm
| Average Burst Failure Leakage Rate | 53 | gallons per minute | Ambrose et al., Life cycle analysis of water networks, https://www.plasticpipe.org/common/Uploaded%20files/1-PPI/Divisions/Municipal%20and%20Industrial/Division%20Publications/Potable%20Water/General/Life%20Cycle%20Analysis%20of%20Water%20Networks%20PP%20XIV%202008%20CSIRO.pdf
| Average Burst Failure Duration | 4320 | mins | Ambrose et al., Life cycle analysis of water networks, https://www.plasticpipe.org/common/Uploaded%20files/1-PPI/Divisions/Municipal%20and%20Industrial/Division%20Publications/Potable%20Water/General/Life%20Cycle%20Analysis%20of%20Water%20Networks%20PP%20XIV%202008%20CSIRO.pdf
| Total length of drinking water pipe that could be replaced with PVC | 1.716 | million mi
Burst Failure Break Rates by Material Type
| Pipe Material | breaks/(100 mi-year) | breaks/year | Million Gallons Lost Per Year
| AC | 10.4 | 29744 | 6810.1862
| CI | 34.8 | 214368 | 49081.6973
| CSC | 3.1 | 2046 | 468.4522
| DI | 5.5 | 33880 | 7757.1648
| PVC | 2.3 | 11132 | 2548.7827
| Steel | 7.6 | 5016 | 1148.4634
| Other | 12.4 | 8184 | 1873.8086
| Total |  | 304370 | 69688.5552
Utah State University, https://digitalcommons.usu.edu/cgi/viewcontent.cgi?article=1173&context=mae_facpub
Burst Failure Break Rates by Material Type (assuming all pipes are plastic)
| Pipe Material | breaks/(100 mi-year) | breaks/year | Million Gallons Lost Per Year
| AC | 2.3 | 6578 | 1506.0989
| CI | 2.3 | 14168 | 3243.9053
| CSC | 2.3 | 1518 | 347.5613
| DI | 2.3 | 14168 | 3243.9053
| PVC | 2.3 | 11132 | 2548.7827
| Steel | 2.3 | 1518 | 347.5613
| Other | 2.3 | 1518 | 347.5613
| Total |  | 50600 | 11585.376
Background Leakage Rates
The research team found no available resources on background leakage rates by material. Therefore the team is using maximum allowable leakage values during hydrostatic testing, based on AWWA Design and Installation Manual Best Practices
| Background leakage - % of loss in system | 10% | % | Utah State University, https://digitalcommons.usu.edu/cgi/viewcontent.cgi?article=1173&context=mae_facpub
| The amount of drinking water that is lost due to leaks across the entire nation annually | 1423.5 | Billion gallons per year
Pipe Failure savings from replacing all drinking water pipes with plastic pipe
| Water savings due to reduced burst failures | 58103.1792 | Million gallons
| Energy savings per year | 81925482.672 | kWh
| Cost savings per year (Energy Costs) | 6922703.2858 | $
| Cost savings per year (Break Repair Costs) | 609048000 | $
| Carbon savings per year | 31950.9382 | Metric tons CO2
Background leakage savings from replacing all drinking water pipes with plastic pipe
| Water savings due to reduced background leakage | 1423500 | Million gallons
| Energy savings per year | 2007135000 | kWh
| Cost savings per year (Energy Costs) | 169602907.5 | $
| Carbon savings per year | 782782.65 | Metric tons CO2
Drinking Water Friction Loss Calculations
Friction Losses
Friction losses refer to the head loss resulting from the friction between the pipe wall and the flowing water, as well as the dissipation of energy due to water viscosity. The calculations used to determine the frictional losses below involve evaluating the impact of deterioration in the friction factor on head loss. This evaluation utilizes the Hazen-Williams equation, with the C factor determined by the annual deterioration rate specific to the pipe. In this study, the flow rate is assumed to be the same for all pipe alternatives within each pressure class, and is based on the volumetric flow rate for PVC pipe at a velocity of 2 feet per second (fps).
Frictional Losses for an 8" Potable Water Pipes Assuming Constant Flow
| Life-Cycle Milestone | Frictional Energy Loss (kWh/mi/ year)
|  | PVC (DR25) | HDPE (DR13.5) | Cement-Lined DI (350 psi)
| Years (1-33) | 6600 | 9768 | 7392 |  | 100 ft = X miles conversion factor
| Years (33-67) | 6864 | 10296 | 11880 |  | 0.018939
| Years (68-100) | 6864 | 10296 | 14784
| Average annual energy loss (kWh/mi/yr) | 6776 | 10120 | 11352
Sustainable Solutions Corporation, https://www.sustainablesolutionscorporation.com/resources
| Assumed annual energy loss for non-plastic pipes | 11352 | kWh/mi/year
| Assumed annual energy loss for plastic pipes | 7110.4 | kWh/mi/year
| Miles of pipe that could be replaced with plastic | 1.716 | Million miles
Annual water/energy/cost/carbon savings due to reduced pipe friction if all pipes were plastic
| Energy savings per year | 7278585600 | kWh
| Cost savings per year (Energy Costs) | 615040483.2 | $
| Carbon savings per year | 2838648.384 | Metric tons CO2
Friction Losses
This is the loss of head caused by pipe wall friction and the viscous dissipation inflowing water. We will use the Darcy-Weisbach equation to calculate friction losses. For this analysis, differences in friction loss will be driven entirely by the piping material's surface roughness.
Minor Losses
Losses due to changes in streamlines is through fittings and appurtenances are taken to be equal to 15% of the total friction losses in the pipes.
Calculating the friction factor, f
The phenomenological Colebrook–White equation (or Colebrook equation) expresses the Darcy friction factor f as a function of Reynolds number Re and pipe relative roughness ε / Dh, fitting the data of experimental studies of turbulent flow in smooth and rough pipes. The equation can be used to (iteratively) solve for the Darcy–Weisbach friction factor f, but we will use the Swamee-Jain equation to determine the f value. The Swamee-Jain equation is valid for turbulent flow in the range: 4,000 less than or equal to NR less than or equal to 10^8 . The flow in sprinkler pipes is almost always turbulent. [4]
Reynolds Number,
Relative Roughness,
Converting head losses into power loss
Pump power to overcome friction losses,
Drinking Water Pipe Size Distributions
| Nominal Diameter | % Distribution
| 3"-8" | 67%
| 10"-12" | 18%
| 14"-24" | 9%
| 27"-36" | 3%
| 42"-48" | 1%
| >48" | 1%
Utah State University, https://digitalcommons.usu.edu/cgi/viewcontent.cgi?article=1173&context=mae_facpub
Pipe Sizes
| Nominal (in) | Inner diameter (m) | Inner area (m^2)
| Mainline - 8" | 0.20272 | 0.032275
Pipe Flow
| Nominal (in) | Flow rate (ft/s) | Volumetric flow rate (m^3/s) |  | Feet to meters conversion
| Mainline - 8" | 5 | 0.049188 |  | 0.3048
Source: American Water Works Association. (2017). AWWA Manual M11: Steel Pipe – A Guide for Design and Installation, 5th edition.
| Pipe Material | Roughness (m) | Surface scaling (m) | Pipe Age (years)
| Plastic Pipe | 4.25e-06 | N/A | 0-40
| New cast iron | 0.000525 | 0 | 1
| rusty cast iron (end of life) | 0.002 | 0.0254 | 20
https://www.engineeringtoolbox.com/surface-roughness-ventilation-ducts-d_209.html
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
|  | Plastic Pipe (year 1-20) | Cast iron year 1 | Cast iron year 2 | Cast iron year 3 | Cast iron year 4 | Cast iron year 5 | Cast iron year 6 | Cast iron year 7 | Cast iron year 8 | Cast iron year 9 | Cast iron year 10 | Cast iron year 11 | Cast iron year 12 | Cast iron year 13 | Cast iron year 14 | Cast iron year 15 | Cast iron year 16 | Cast iron year 17 | Cast iron year 18 | Cast iron year 19 | Cast iron year 20
| Q (m^3/s) | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188 | 0.049188
| L (m) | 1 | bar: 1 to 20
| ID (m) | 0.20272 | 0.20272 | 0.20138 | 0.20004 | 0.19871 | 0.19737 | 0.19603 | 0.1947 | 0.19336 | 0.19202 | 0.19069 | 0.18935 | 0.18801 | 0.18668 | 0.18534 | 0.184 | 0.18266 | 0.18133 | 0.17999 | 0.17865 | 0.17732
| V (m/s) | 1.524 | 1.524 | 1.5443 | 1.565 | 1.5861 | 1.6077 | 1.6297 | 1.6522 | 1.6751 | 1.6985 | 1.7224 | 1.7468 | 1.7717 | 1.7972 | 1.8232 | 1.8498 | 1.877 | 1.9047 | 1.9331 | 1.9622 | 1.9919
| υ (m^2*s) | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06 | 1.0445e-06
| ρ (kg/m^3) | 1 | bar: 1 to 20
| ε (m) | 4.25e-06 | 0.000525 | 0.00060263 | 0.00068026 | 0.00075789 | 0.00083553 | 0.00091316 | 0.00099079 | 0.0010684 | 0.0011461 | 0.0012237 | 0.0013013 | 0.0013789 | 0.0014566 | 0.0015342 | 0.0016118 | 0.0016895 | 0.0017671 | 0.0018447 | 0.0019224 | 0.002
| g (m^2/s) | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81 | 9.81
| η (-) | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71 | 0.71
| Re (-) | 295779.1456 | 295779.1456 | 297742.6421 | 299732.3817 | 301748.894 | 303792.7232 | 305864.428 | 307964.5827 | 310093.7774 | 312252.6185 | 314441.7296 | 316661.7518 | 318913.3445 | 321197.186 | 323513.9742 | 325864.427 | 328249.2836 | 330669.305 | 333125.2747 | 335617.9997 | 338148.3113
| Relative Roughness (-) | 2.0965e-05 | 0.0025898 | 0.0029925 | 0.0034006 | 0.0038141 | 0.0042333 | 0.0046582 | 0.0050889 | 0.0055256 | 0.0059683 | 0.0064173 | 0.0068726 | 0.0073344 | 0.0078027 | 0.0082779 | 0.0087599 | 0.009249 | 0.0097454 | 0.010249 | 0.01076 | 0.011279
| f (-) | 0.014651 | 0.025686 | 0.026656 | 0.02757 | 0.02844 | 0.029273 | 0.030074 | 0.030848 | 0.031599 | 0.032331 | 0.033045 | 0.033743 | 0.034428 | 0.035102 | 0.035765 | 0.036419 | 0.037065 | 0.037703 | 0.038336 | 0.038963 | 0.039585
| Hf (m) | 0.0085555 | 0.015 | 0.016089 | 0.017205 | 0.018353 | 0.019538 | 0.020767 | 0.022043 | 0.023371 | 0.024756 | 0.026202 | 0.027714 | 0.029297 | 0.030955 | 0.032694 | 0.034519 | 0.036435 | 0.03845 | 0.040568 | 0.042797 | 0.045144
| Hm (m) | 0.0012833 | 0.0022499 | 0.0024134 | 0.0025807 | 0.0027529 | 0.0029308 | 0.0031151 | 0.0033065 | 0.0035057 | 0.0037134 | 0.0039304 | 0.0041572 | 0.0043946 | 0.0046433 | 0.0049041 | 0.0051778 | 0.0054653 | 0.0057674 | 0.0060852 | 0.0064196 | 0.0067717
| P (W) | 0.13594 | 0.23834 | 0.25565 | 0.27338 | 0.29162 | 0.31046 | 0.32998 | 0.35025 | 0.37136 | 0.39336 | 0.41634 | 0.44037 | 0.46551 | 0.49186 | 0.51949 | 0.54848 | 0.57894 | 0.61094 | 0.6446 | 0.68002 | 0.71732
| Operating Hours (hrs/yr) | 8760
| Energy consumption (kWh/year/m) | 1.1908 | 2.0878 | 2.2395 | 2.3948 | 2.5546 | 2.7196 | 2.8906 | 3.0682 | 3.2531 | 3.4459 | 3.6472 | 3.8576 | 4.0779 | 4.3087 | 4.5507 | 4.8047 | 5.0715 | 5.3519 | 5.6467 | 5.957 | 6.2837
| Energy savings (kWh/year/m) | N/A | 0.89697 | 1.0487 | 1.2039 | 1.3637 | 1.5287 | 1.6997 | 1.8774 | 2.0623 | 2.255 | 2.4563 | 2.6668 | 2.887 | 3.1178 | 3.3599 | 3.6139 | 3.8806 | 4.161 | 4.4559 | 4.7662 | 5.0929
𝐻_𝑓=(𝑓𝑙𝑉^2)/2𝑔𝐷
𝐻_𝑓=ℎ𝑒𝑎𝑑 𝑙𝑜𝑠𝑠 𝑑𝑢𝑒 𝑡𝑜 𝑓𝑟𝑖𝑐𝑡𝑖𝑜𝑛 𝑡ℎ𝑎𝑡 ℎ𝑎𝑠 𝑡ℎ𝑒 𝑢𝑛𝑖𝑡 𝑜𝑓 𝑙𝑒𝑛𝑔𝑡ℎ
𝑓=𝑓𝑟𝑖𝑐𝑡𝑖𝑜𝑛 𝑓𝑎𝑐𝑡𝑜𝑟, 𝑢𝑛𝑖𝑡𝑙𝑒𝑠𝑠
L=𝑙𝑒𝑛𝑔𝑡ℎ 𝑜𝑓 𝑡ℎ𝑒 𝑝𝑖𝑝𝑒
D=𝑖𝑛𝑡𝑒𝑟𝑛𝑎𝑙 𝑑𝑖𝑎𝑚𝑒𝑡𝑒𝑟
V=𝑎𝑣𝑒𝑟𝑎𝑔𝑒 𝑣𝑒𝑙𝑜𝑐𝑖𝑡𝑦
g=𝑔𝑟𝑎𝑣𝑖𝑡𝑎𝑡𝑖𝑜𝑛𝑎𝑙 𝑎𝑐𝑐𝑒𝑙𝑒𝑟𝑎𝑡𝑖𝑜𝑛
𝑅𝑒= 𝑉𝐷/𝜐
𝜈=𝑘𝑖𝑛𝑒𝑚𝑎𝑡𝑖𝑐 𝑣𝑖𝑠𝑐𝑜𝑠𝑖𝑡𝑦
= 𝜀/𝐷
𝜀=𝑟𝑜𝑢𝑔ℎ𝑛𝑒𝑠𝑠
𝑃=(𝜌𝑔〖(𝐻〗_𝑓+𝐻_𝑚))/𝜂
P=𝑝𝑢𝑚𝑝 𝑝𝑜𝑤𝑒𝑟
η=𝑝𝑢𝑚𝑝 𝑒𝑓𝑓𝑖𝑐𝑖𝑒𝑛𝑐𝑦
𝜌=𝑑𝑒𝑛𝑠𝑖𝑡𝑦
𝐻_𝑚=0.15∗𝐻_𝑓
𝐻_𝑚=𝑚𝑖𝑛𝑜𝑟 𝑙𝑜𝑠𝑠𝑒𝑠 𝑡ℎ𝑎𝑡 ℎ𝑎𝑠 𝑡ℎ𝑒 𝑢𝑛𝑖𝑡 𝑜𝑓 𝑙𝑒𝑛𝑔𝑡ℎ
The research team did not find reliable data on the distribution of wastewater pipe materials
There is very limited data on pipe material life cycle costs. Due to the wide variety of factors the team is only publishing an conservative % cost savings estimate
There is wide variation in data on pipe material life cycle assessments. Due to the wide variety of factors the team published a conservative % emissions reduction estimate based on available data
It is unclear why the sustainable solution corporation LCA embodied carbon estimates are and order of magnitude less the the Fei Du et. al. report
512 metric tons CO2 /mi vs 39-50.7 metric tons CO2

## Research - Pumps
Drinking Water and Wastewater Pumping System Research
The blue cells in this workbook are assumptions. The text boxes to the right of the tables provide context/rationale for these assumptions.
= Data inputs the team identified as having uncertainty and were vetted with SMEs
Load Factor and Load Type Distribution
This section presents the distribution of pumping energy consumption by load type and load factor from DOEs MSMA.
Load Type | Load Factor Range | Load Factor | Energy Consumption, GWh (2018)
|  |  | Full Industrial Sector | Wastewater | Water Treatment
Constant Load | <= 0.4 | 0.4 | 2999 | 0 | 0%
| 0.4 < x < 0.75 | 0.75 | 36938 | 353 | 19%
| => 0.75 | 0.9 | 129361 | 3304 | 81%
Variable Load | <= 0.4 | 0.4 | 29451 | 539 | 13%
| 0.4 < x < 0.75 | 0.75 | 183998 | 4246 | 67%
| => 0.75 | 0.9 | 71950 | 795 | 20%
Unknown if Variable |  |  | 92266 | 18661 | NA
TOTAL |  |  | 546963 | 27898
Source: Motor System Market Assessment; https://motors.lbl.gov/analyze/7-0b3a
Load Type | % of Energy Consumption
| Full Industrial Sector | Wastewater | Water Treatment
Constant Load | 54% | 43% | 48%
Variable Load | 46% | 57% | 52%
VFD Saturation
This section presents the distribution of pumping energy by control type and calculates a saturation of VFD (as % of energy consumption).
Control Type | Energy Consumption, GWh
| Full Industrial Sector | Wastewater | Water Treatment
Unable to collect | 6576 | 5 | Unknown
None | 79607 | 14885 | Unknown
Other | 1217 | 0 | Unknown
VFD | 28468 | 2467 | Unknown
Total | 115868 | 17357 | Unknown
Source: Motor System Market Assessment; https://motors.lbl.gov/analyze/47-0j0d84
Control Type | % of Energy Consumption
| Full Industrial Sector | Wastewater | Water Treatment
VFD Control | 26.05% | 14.22% | 50%
Other Control | 1.114% | 0% | 0%
No Control | 72.84% | 85.78% | 50%
Total | 100% | 100% | 100%
Pump Type Distribution (Rotodynamic vs Positive Displacement)
This section presents the distribution of pumping energy between positive displacement pumps and rotodynamic pumps.
% of Energy Consumption
Pump Type | Full Industrial Sector | Wastewater | Water Treatment
Rotodynamic | 81% | 85% | 90%
Positive Displacement | 19% | 15% | 10%
Total | 100%
Source: Motor System Market Assessment Volume 1, Figure 22, Page 37; https://motors.lbl.gov/
Pump Efficiency
This section presents the average change in pump efficiency that can be seen by installing a high-efficiency pump. This table holds a separate value for different pump sizes.
Pump Size | ΔPump Efficiency
200 HP and Smaller | 4%
Greater than 200 HP | 0.5%
Pump Size
This section presents the distribution of pump sizes based on data from DOEs MSMA. This table holds a separate value for rotodynamic pumps and positive displacement pumps.
Pump Type | ΔPump Efficiency
| Full Industrial Sector | Wastewater | Water Treatment
200 HP and Smaller | 58% | 26.75% | 26.75%
Greater than 200 HP | 42% | 73.25% | 73.25%
Average VFD Efficiency
This section presents the average efficiency of a VFD, for different power output values and rated HPs. The energy savings calculations assume a straight average across all values presented in the table below.
Average VFD efficiency | 94.94%
Variable Drive HP Rating | Percent of Drive Rated Power Output
| 25 | 50 | 75 | 100
5 | 88 | 92 | 94 | 95
10 | 90 | 94 | 95 | 96
20 | 93 | 95 | 96 | 97
30 | 93 | 95 | 96 | 97
50 | 92 | 95 | 96 | 97
60 | 92 | 95 | 96 | 97
75 | 93 | 96 | 97 | 97
100 | 94 | 96 | 97 | 97
200 | 95 | 96 | 97 | 97
Source: DOE Advanced Manufacturing Office, Motor Systems Tip Sheet #11, Adjustable Speed Drive Part Load Efficiency, https://www.energy.gov/sites/prod/files/2014/04/f15/motor_tip_sheet11.pdf
Power Load Relationships
This section presents the relationship between motor power draw and system load for pumps operating with two different control strategies. These relationships take the form of the equation , with the coefficients listed in the table below.
NREL Pump Default Curve Correlation Coefficients
Pump Control Strategy | Coeff | Pump Type
Centrifugal
Throttle Control | A | 0.55218
| B | 0.63701
| C | -0.18996
VFD | A | 0.21976
| B | -0.87478
| C | 1.6526
NREL: The Uniform Methods Project: Methods for Determining Energy Efficiency Savings for Specific Measures. Chapter 18: Variable Frequency Drive Evaluation Protocol, Table 2, Page 12, https://www.nrel.gov/docs/fy17osti/68574.pdf
Control Type | Load Point
| 25% | 50% | 75% | 100%
Throttle Control | 69.96% | 82.32% | 92.31% | 99.92%
VFD Control | 10.44% | 19.55% | 49.33% | 99.76%
Load Profiles and Load Factor
This section estimates the load profile for each variable load load factor and calculates the "Load Profile Factor", and the product of the load profile and the power load relationship for each control strategy.
Industrial Sector Load Profile
| Load Point |  |  |  | Load Factor
Load Profile | 25% | 50% | 75% | 100%
Variable Load | 15.7% | 26.3% | 11.5% | 46.3% | 0.71999
BPA Market Model, https://www.bpa.gov/energy-and-services/efficiency/market-research-and-momentum-savings/adjustable-speed-drives-market-research
Wastewater - Adjusted Load Profiles, to represent assumed Load Factors
Load Factor | Load Point |  |  |  | Weighting, based on % of energy for wastewater
| 25% | 50% | 75% | 100%
0.4 | 65% | 15% | 15% | 5% | 9.659%
0.75 | 10% | 30% | 10% | 50% | 76.09%
0.90254 | 5.234% | 8.766% | 5.75% | 80.25% | 14.25%
Weighted average load profile | 14.63% | 25.53% | 9.877% | 49.96% | 0.73792
Load Factor | Load Profile Factor, by control type
| No Control | VFD
0.4 | 0.76662 | 0.22103
0.75 | 0.90884 | 0.6172
0.9 | 0.96374 | 0.85152
Pump Application Distribution
This section presents the disaggregation of electricity by application for Wastewater and Water Treatment facilities.
Wastewater Electricity Consumption, by application
Pump Application | % of Pumping Electricity Consumption
Pumping | 12%
Aeration | 53%
Biosolids | 30%
Sludge | 2.5%
Other | 2.5%
Total | 100%
https://www.hansenallenluce.com/wp-content/uploads/2015/11/Energy-Use-Water-Sector.pdf
Water Treatment Pumping Electricity Consumption, by pump application
Pump Application | % of Pumping Electricity Consumption
Distribution Pumping | 67%
In-Plant Water Pumping | 8%
Water Intake Pumping | 11%
Water Treatment | 14%
Total | 100%
https://www.hansenallenluce.com/wp-content/uploads/2015/11/Energy-Use-Water-Sector.pdf
Water Pumping Energy Intensity
This section includes energy intensity values for different systems
Information | Value | Units
Water Treatment Pumping Energy intensity | 1150 | kWh/million gal
Wastewater system energy intensity | 1900 | kWh/million gal
https://www.hansenallenluce.com/wp-content/uploads/2015/11/Energy-Use-Water-Sector.pdf
𝑦=𝑎+𝑏𝑥+𝑐𝑥^2

## Research - Pipes
Drinking Water and Wastewater Piping Systems Research
This tab includes the research finding for drinking water and wastewater piping systems. The research findings on this tab are used as inputs in the 'Piping Calculation' tab.
Life Cycle Assessment of PVC Water and Sewer Pipe and Comparative Sustainability Analysis of Pipe Materials, 2017
https://www.uni-bell.org/files/Reports/Life_Cycle_Assessment_of_PVC_Water_and_Sewer_Pipe_and_Comparative_Sustainability_Analysis_of_Pipe_Materials.pdf
This report includes
Thorough examination of a PVC pipe Life Cycle Assessment (LCA) for seven pipe products
Comparisons to other piping materials regarding performance and durability attributes
Cradle-to-grave life cycle stages, which include
Extraction and processing of raw materials
manufacturing
transportation and distribution
installation, use, and maintenance
Recycling and final disposal
For this study, DI pipe is assigned a 50-year service life based on failure data of DI pipes and the fact that new ductile iron pipes have much thinner walls than older iron pipes and lack independent dig-up and pipe material testing studies.
PVC pipe is assigned a 100-year service life based on 60 years of experience, extensive industry studies, dig-up field samples and historical data demonstrating low failure and water main break rates.
Since there is very little data on the actual longevity and performance of newer HDPE pipe with thinner walls, a 50- year service life was assumed due to the potential for oxidation, strain creep and reduced Safety Factor.
TABLE 3.1 : PVC PIPE PRODUCTS UNDER THE SCOPE OF THE LCA
Application | Standard | Nominal Diameter | Dimension Ratio/ Pipe Stiffness | Average Weight* (lb./ft.)
Potable Water | AWWA C900 | 8" | DR18 | 9.1
| AWWA C900 | 8" | DR25 | 6.7
| AWWA C905** | 24" | DR25 | 55.9
Storm Water | ASTM F794 AASHTO M304 | 24" Profile Wall | PS46 | 19.2
Sanitary Sewer | ASTM F794 | 8" Profile Wall | PS46 | 2.5
| ASTM D3034 | 8" Solid Wall | PS46 | 4.3
| ASTM F679 | 24" Solid Wall | PS46 | 38.7
Table 4.2: Overall Cradle-through-installation Life Cycle GHG Emission Impact of PVC Pipe (kg CO2 Eq per 100')
Life Cycle Stage | 8" DR25 PC165 C900 | 8" PS46 SDR35 D3034 Solid Wall
Raw Materials | 680 | 400
Raw Material Transportation | 9 | 8
Pipe Manufacturing | 77 | 73
Packaging | 2 | 2
Final Product Transportation | 15 | 8
Installation | 178 | 250
Total | 960 | 740
Table 8.5 Effects of Friction Factor Deterioration on Head Loss for an 8" Potable Water Pipe Assuming Constant Flow
| Hazen-Williams Coefficients |  |  | Frictional Energy Loss (kWh/100 ft/ year)
Life-Cycle Milestone | PVC (DR25) | HDPE (DR13.5) | Cement-Lined DI (350 psi) | PVC (DR25) | HDPE (DR13.5) | Cement-Lined DI (350 psi)
Install | 155 | 155 | 140 | 125 | 185 | 140
50 Years | 150 | 150 | 110 | 130 | 195 | 225
100 Years | 150 | 150 | 95 | 130 | 195 | 280
Appendix: Pressure Pipe
For the purposes of this study the flow rate was assumed to be common to all pipe alternatives within each pressure class based on the volumetric flow rate for PVC pipe at 2 fps of velocity
Table A.2: Water Loss Volume per Year and 100 Year Water Loss Embodied Energy
Pipe Material | PVC Size/DR/PC | Flow Rate (gpm) | Break Time (min) | Failure Rate (#/100/yc.) | Annual Loss Volume (gal/100)yr.) | Treated Water Embodied Energy (kWh/Mgal) | 100-Year Water Loss Embodied Energy (kWh/100')
PVC | 8"/18/235 | 312 | 240 | 0.000492 | 36.9 | 1410 | 5.2
| 24/25/165 | 2730 | 240 | 0.000492 | 322.6 | 1410 | 45.5
DI | 8"/-/350 | 312 | 240 | 0.000928 | 69.5 | 1410 | 9.8
| 24"/-/200 | 2730 | 240 | 0.000928 | 608 | 1410 | 85.7
HDPE | 8'/9.0/250 | 312 | 240 | 0.000492 | 36.9 | 1410 | 5.2
| 24'/13.5/160 | 2730 | 240 | 0.000492 | 322.6 | 1410 | 45.5
PCCP | 24"/-/200 | 2730 | 240 | 0.001023 | 670 | 1410 | 94.5
Water Main Break Rates In the USA and Canada: A Comprehensive Study
Utah State University, https://digitalcommons.usu.edu/cgi/viewcontent.cgi?article=1173&context=mae_facpub
This study provides key inputs to water asset management’s life-cycle cost analysis through a comparison of break-rates of commonly used pipe materials.
There are approximately 155,693 public water systems in the United States with 52,110 community water systems providing year-round water services for residents.
According to another WaterRF publication, the average pipe break rate (regardless of cause) for water utilities is between 21 to 27 breaks per 100 miles of pipeline per year. An additional WaterRF study cited an average of 25 breaks per 100 miles per year. Although water utilities typically take action to manage and reduce pipe breaks through monitoring, preventing all pipe failures is impossible (WaterRF, Knowledge Portals, 2017).
Based on an EPA report, there are approximately 880,000 miles of distribution pipe in the USA (EPA, 2007). Other EPA reports (EPA, 2002 and EPA, 2013) estimate the amount of installed water main pipe in the USA at over 1 million miles and 1.5 million miles. Using the above result of 308 people/ mile of water main and the current US population of 326.0 million, this produces an estimate of 1.06 million miles of pipe. Currently, a commonly cited value for the length of water mains in the US is 1.2 million miles (Walton, 2016).
Number of public water systems in the United States |  | 207803
Length of water mains in the United States |  | 1.2 | Million Miles
US Population |  | 326 | Million
Average people serviced for each mile of water main installed |  | 271.6667
PERCENT OF TOTAL LENGTH OF PIPE SEPARATED BY MATERIAL TYPE
AC | 13%
CI | 28%
CSC | 3%
DI | 28%
HDPE | 0.5%
PVC | 22%
PVCO | 0.05%
Steel | 3%
Other | 0.8%
Unknown | 2%
*Based on data from figure 10
There is so little HDPE pipe (859 miles) and PVCO pipe (83 miles) in this survey, that these two pipe materials will be added to the of the “Other” category in the remainder of this report.
PERCENT OF TOTAL LENGTH OF PIPE BY PIPE DIAMETER FROM THE DETAILED SURVEY
3"-8" | 67%
10"-12" | 18%
14"-24" | 9%
27"-36" | 3%
42"-48" | 1%
>48" | 1%
*Based on data from figure 15
BREAK RATES OF EACH PIPE MATERIAL FROM THE BASIC SURVEY (breaks/(100 mi-year))
AC | 10.4
CI | 34.8
CSC | 3.1
DI | 5.5
PVC | 2.3
Steel | 7.6
Other | 12.4
*Based on data from figure 20
Water loss due to leakage is reaching critical levels where in some cases 20% to 30% of water is leaking from water mains (New Jersey 101.5, 2017). The basic survey asked what percentage of water volume input to the system is water loss (due to leakage). A total of 201 utilities were able to provide a water loss value. The reported average leakage from the basic survey was 10% with a standard deviation of 7.7%.
Life Cycle Analysis for Water and Wastewater Pipe Materials, 2013
Fei Du, S.M.ASCE; Gwendolyn J. Woods, S.M.ASCE; Doosun Kang; Kevin E. Lansey, A.M.ASCE; and Robert G. Arnold, M.ASCE
https://ascelibrary.org/doi/10.1061/%28ASCE%29EE.1943-7870.0000638
A life cycle analysis (LCA) was performed for six commonly used types of water and wastewater pipe materials: polyvinyl chloride (PVC), ductile iron, cast iron, high density polyethylene (HDPE), concrete, and reinforced concrete. The objectives were to:
(1) compare the six pipe materials in terms of global warming potential (GWP) through four LCA phases: pipe production, transport, installation, and use
(2) determine the primary source(s) of differences in LCA results; and (3) examine the effectiveness of currently used pipe size selection criteria when LCA GWP is considered.
(3) examine the effectiveness of currently used pipe size selection criteria when LCA GWP is considered.
Four phases were modeled in terms of their contributions to GWP: pipe production, transport, installation, and use.
The functional unit to present and compare LCA results was unit pipeline length (km), as opposed to more commonly used functional units based on the volume of water produced or delivered.
Table 4 Material-Specific Embodied Energies for the Pipe Materials Investigated
Material | Embodied Energy (MJ/kg)
Ductile Iron | 34.4
Cast Iron | 25.5
PVC | 75.2
HDPE | 74.9
Reinforced concrete | 3.5
Concrete | 1.34
Embodied energy includes the energy expended for raw material acquisition and all processes necessary for material production; that is, all energy consumed up to the point at which materials (in this case, finished pipes) leave the factory.
Table 5 Summary of GWP per km for 12" Diameter Pipe of Different Materials
Pipe materials (12-in pipe) | Total GWP (10^3 kg CO2/km) | Production | Installation | Transportation
PVC | 318 | 315 | 2.81 | 0.26
Ductile Iron | 472 | 468 | 3.28 | 0.88
Concrete | 68.3 | 63.1 | 2.91 | 2.26
HDPE | 218 | 215 | 2.81 | 0.17
Reinforced Concrete | 152 | 146 | 2.91 | 2.47
Cast Iron | 353 | 349 | 3.28 | 0.84
EPA: State of Technology Report for Force Main Rehabilitation, 2010
Kalyan R. Piratla, S.M.ASCE; Samuel T. Ariaratnam, M.ASCE; and Aaron Cohen
Force mains represent about 7.5% of the wastewater system
The approximate length of the force main system in the US is 60,000 miles (96561 km).
Polyethylene plastic pipe systems vs ductile iron environmental impact comparison
TEPPFA LIFE CYCLE ASSESSMENT
https://www.teppfa.eu/wp-content/uploads/LCA3_PW-Leaflet-PE-vs-DI.pdf
For the purposes of a direct fair comparison between alternative materials the following identical functional units were used in the LCA study for pressurized water supply systems:
- below ground pressure transportation of drinking water over a distance of 100 meters from the exit of the water plant to the water meter in a building
- assuming a service lifetime for the pipe system of 100 years
LIFE CYCLE ANALYSIS OF WATER NETWORKS
Proceedings of the 14th Plastics Pipes Conference, PXIV September 22-24, 2008, Budapest, Hungary
https://www.plasticpipe.org/common/Uploaded%20files/1-PPI/Divisions/Municipal%20and%20Industrial/Division%20Publications/Potable%20Water/General/Life%20Cycle%20Analysis%20of%20Water%20Networks%20PP%20XIV%202008%20CSIRO.pdf
Background Leakage
Background leakage occurs from small leaks at joints between pipe lengths and at property connections (
For sections of pipeline without property connections, the AWWA models for maximum allowable leakage during hydrostatic testing AWWA M23 for PVC (16) and AWWA M41 for DI (17) were adopted, the latter with modifications to factor in effects of ageing.
Burst Failure Leakage
International Water Association (IWA) studies have shown (15) that 95% of burst leakage events are reported, and on average the leakage losses from each event aggregates to12m3/hour (53 gallons/minute) for 3 days at a nominal 500kPa (72psi) operating pressure before the leak is repaired.
Average burst failure leakage rate | 53 | gal/min
Average burst failure duration | 4320 | minutes
A Framework for Holistic Life Cycle Cost Analysis for Drinking Water Pipelines
https://vtechworks.lib.vt.edu/bitstream/handle/10919/78357/Khurana_M_T_2017.pdf?sequence=1
This research has been aimed at providing a framework for holistic life cycle cost analysis of drinking water pipelines which includes both life cycle cost analysis and life cycle assessment.
the methodology of this research starts by developing a comprehensive cost structure and then using that cost structure to develop the holistic life cycle cost analysis model.
estimated values of different technologies and other costs have been provided with the help of literature and previous academic and water industry surveys.
This model has the capability to compare five scenarios including comparison of different pipe materials, installation technologies, condition assessment technologies, rehabilitation technologies and replacement technologies and methods.
A comparison was made between the life cycle costs of two pipe materials considering 50 years of analysis period
Climate Impact of Plastics
https://www.mckinsey.com/~/media/mckinsey/industries/chemicals/our%20insights/climate%20impact%20of%20plastics/climate-impact-of-plastics_vf.pdf
McKinsey report indicates that GHG contribution of PVC is 35-40% less than Concrete or ductile Iron
Lowering Costs in Water Infrastructure through Procurement Reform: A Strategy for State Governments
https://www.uni-bell.org/Portals/0/ResourceFile/lowering_costs_in_water_infrastructure_alec_final.pdf?ver=2018-05-25-095636-310
Leaking pipes also lose an estimated 2.6 trillion gallons of drinking water every year, or 17 percent of all water pumped in the United States. This represents $4.1 billion in wasted electricity every year
As a result of widespread corrosion in the system, there are more than 300,000 annual water main breaks in North America
Estimated Drinking Water Lost to Leakage | 2.6 | trillion gal
Estimated Wasted Electricity due to Leakage | 4.1 | $ billion
Corrosion mitigation annual costs* | 50.7 | $ billion
*Costs for water/wastewater including repairs, lost water, pipe replacements, and implementation of expensive corrosion mitigation programs
PVC vs Ductile Iron Pipe Installed Cost Comparison Calculator
Source: https://www.jmeagle.com/pvc-vs-ductile-iron-pipe-installed-cost-comparison-calculator
Cost for 8' pipes per LF
| C900/C905 PVC | DI
Material Cost | 6.3 | 18.384
Labor & Equipment Cost | 5.728 | 6.5872
Backfill Cost | 5.8337 | 5.8337
TCO | -
Total Cost of Ownership: PVC-U vs. other pipe materials
https://pvc4pipes.com/wp-content/uploads/2019/06/PVC-U_pipe_competitiveness_TCO_Althesys-fact-sheet_final.pdf
Cost of Ownership (€/m)
Material | Purchase | Installation
Diameter = 315 mm
PVC | 30.5 | 92.1
DI | 56.1 | 100.1
Water Mains: Replacement and Maintenance
Source: https://city.milwaukee.gov/water/customer/WatermainsReplacementandMaintenance.htm
Average Cost to Repair Water Main | 2400 | $
The Carbon Footprint of Water
A 5% reduction in water distribution system leakage would save 270 MGD of water and 313 million kWh of electricity annually, equal to the electricity use of over 31,000 homes. In addition, approximately 225,000 metric tons of CO2 emissions could be avoided
Water Leakage Reduction | 270 | Mgal/day
Annual Water Leakage Reduction | 98550 | Mgal
Annual Associated Electricity Savings | 313 | million kWh
Annual Avoided C02 | 225000 | metric tons
Avoided CO2 per Mgal of water | 2.2831 | metric tons/Mgal
Electricity Savings per Mgal of water | 0.0031761 | kWh/Mgal
Source: https://www.csu.edu/cerc/researchreports/documents/CarbonFootprintofWater-RiverNetwork-2009.pdf
American Waterworks Association (AWWA) -PVC Pipe Design and Installation, Third Edition
This is a book, I was only able to get Chapter 1.
AWWA’s† PVC pipe and fittings standards define the basic properties of PVC compound using the American Society for Testing and Materials‡ (ASTM)
Specification D1784, Standard Specification for Rigid Poly(Vinyl Chloride) (PVC) Compounds and Chlorinated Poly(Vinyl Chloride) (CPVC) Compounds.
The specification includes a five digit cell class designation system by which PVC compounds are classified according to their physical properties
Fusible PVC pipe has been installed in North America since 2004..
Molecularly oriented polyvinyl chloride (PVCO) pressure pipe has been installed in Europe since the early 1970s and in North America since 1991.
PVC/PVCO pipes (nonconductor) are resistant to almost all types of corrosion (both chemical and electrochemical) that are experienced in
underground piping systems, consequently no lining, coating, cathodic protection or plastic encasement is required
Resistant to biological attack (microorganisms)
Source: https://www.awwa.org/Portals/0/Awwa/Publishing/Manuals/M23ed3LookInside.pdf?ver=2020-05-27-132852-560

## Piping Health Benefits (hidden)
PVC Pipe Association - PVC vs. Ductile Iron (DI) Pressure Pipe for Water Mains
PVC is immune to internal corrosion, so no liners are needed to maintain water quality and flow characteristics
PVC is immune to external corrosion, so no coatings, plastic encasement, or cathodic protection are needed.
Source: https://www.uni-bell.org/Portals/0/ResourceFile/pvc-vs-ductile-iron-di-pressure-pipe-for-water-mains.pdf
American Waterworks Association (AWWA) -PVC Pipe Design and Installation, Third Edition
PVC/PVCO pipes (nonconductor) are resistant to almost all types of corrosion (both chemical and electrochemical) that are experienced in
underground piping systems, consequently no lining, coating, cathodic protection or plastic encasement is required.
PVC pipe will not deteriorate or break down under attack from bacteria or other microorganisms, nor will it serve as a nutrient to microorganisms, macroorganisms, or fungi.
Source: https://www.awwa.org/Portals/0/Awwa/Publishing/Manuals/M23ed3LookInside.pdf?ver=2020-05-27-132852-560
Overview of Piping Systems and their Seismic Vulnerability
Modern pipe systems such as ductile iron and PVC are suitable for installations where moderate levels of wave propagation (ground shaking) are expected.
In summary, earthquakes are damaging to buried pipelines. Liquefaction and associated lateral spreading (PGD) has resulted in the highest damage rates. Cast iron pipe is vulnerable particularly because of its brittle joints, but modern pipelines with unrestrained joints such as ductile iron are vulnerable to joint separation when subjected to PGD.
Source: https://responsiblechoice.info/wp-content/uploads/Overview-of-Piping-Systems-and-their-Seismic-Vulnerability.pdf
Water Main Break Rates In the USA and Canada: A Comprehensive Study
Utah State University, https://digitalcommons.usu.edu/cgi/viewcontent.cgi?article=1173&context=mae_facpub
Canada can have very corrosive soils (Seargeant, 2013) and this is reflected in the high break rates of cast and ductile iron pipes in Figure 25. Seargeant reported that the highly corrosive soil in Edmonton necessitated a transition from cast iron to asbestos cement pipes in 1966 and then to PVC starting in 1977. The transition to PVC has produced a dramatic reduction in water main break rates for the city.
North America’s Cinderella Pipe Story: A Look at PVC Pipes’ Climb to the Top
tests demonstrate that PVC pipes provide excellent antimicrobial performance and protection against bio-film formation
PVC pipes present an effective barrier to “permeation of benzene, toluene, and xylenes in either gasoline vapors or gasoline contaminated groundwater at typical contaminated sites”
Over four decades of testing and certified compliance have verified that PVC pipes do not exhibit significant reaction with even aggressive drinking water and are arguably the safest of all common pipe materials.
Source: https://dnr.wisconsin.gov/sites/default/files/topic/Wells/PVCStudyGroup/PVCPipesClimbtoTopPaper.pdf

## Summary of Approach (hidden)
Summary of Findings
This tab summarizes the research team's research approach for water and wastewater savings opportunities. This tab answers the following questions:
What underlying data do we need to calculate the stats listed on the 'Designed Deliverable Framework' Tab?
Where can we find this data?
Are there data gaps?
What assumptions are we going to make to fill these data gaps?
Constants and Equivalencies
Value | Where are we going to find this information?
Electricity cost ($/kWh) | https://www.eia.gov/electricity/data.php#sales
Carbon intensity (CO2e/kWh) | https://www.eia.gov/environment/emissions/carbon/#:~:text=Between%202005%20and%202021%2C%20the,to%200.39%20mt%20per%20megawatthour
Social cost of carbon ($/CO2e) | https://www.epa.gov/sites/default/files/2016-12/documents/social_cost_of_carbon_fact_sheet.pdf
Pipe density (or pipe weight to pipe length conversion) (ft/kg) | https://ascelibrary.org/doi/10.1061/%28ASCE%29EE.1943-7870.0000638
Raw data details
Pumping Systems - Raw Data Needs |  | Where are we going to find this information? |  | Notes
Value | Dimension | Waste Water | Water Supply/Treatment | Waste Water | Water Supply/Treatment
Number of pumps |  | Data Gap We don’t necessarily need to know number of pumps. If we know the total energy consumption and the percent savings potential associated with each opportunity, we can calculate the energy savings without knowing the number of pumps
Distribution of pumping applications (i.e. where are pumps used) |  | Data gap | Quantifying Energy Use in the U.S. Public Water Industry Report | Vet with SME
Distribution of pump type (i.e. constant torque vs variable torque) | pump application | 2018 MSMA; Torque-type is not waste water specific | Data gap | double MSMA % CT for water treatment and half the MSMA % CT for water conveyance; Vet MSMA value with SME;
Load profile distribution (i.e. constant load vs variable load) | pump application | 2018 MSMA | Data gap |  | Vet with SME
ASD saturation | pump application | 2018 MSMA | Data gap |  | Vet with SME
Pump efficiency distribution | pump application | DOE Pumps TSD; Not W/WW specific |  | Vet with SME
Average pumping energy intensity (kWh/million gal) |  | Data gap | Quantifying Energy Use in the U.S. Public Water Industry
National pumping energy use (TWh) | pump application | 2018 MSMA | Calculate this value with information from EIA, EPRI, and one other source listed below
Avg pump horsepower | pump application | 2018 MSMA | Data gap
Avg pump efficiency | pump application | DOE Pumps TSD; Not W/WW specific
Avg. motor efficiency | pump application | DOE Motors TSD
Avg. load factor | pump application | 2018 MSMA | Data gap
Avg. operating hours | pump application | 2018 MSMA | Data gap
% ASD energy savings | Pump application; load type | BPA ASD Market Model; Not W/WW specific |  | Think through how we will modify assumptions for industrial sector to W/WW
% efficient pump energy savings | pump application | Data gap |  | Vet with SME
Incremental efficient pump costs |  | DOE Pumps TSD; Not W/WW specific |  | Vet with SME
Incremental VFD costs |  | RTF Measures have incremental cost for VFDs
Real world haircuts |  | N/A, identified after/with experts |  | Vet with SME
Piping Systems - Raw Data Needs |  | Where are we going to find this information? |  | Notes
Value | Dimension | Waste Water | Water Supply/Treatment | Waste Water | Water Supply/Treatment
Water consumed/processed in US annually |  | EPA; https://www.epa.gov/nutrientpollution/sources-and-solutions-wastewater | Water Main Break Rates In the USA and Canada: A Comprehensive Study)
Length of pipe | pipe material | EPA Clean Watersheds Needs Survey 2012 Report to Congress | Water Main Break Rates In the USA and Canada: A Comprehensive Study)
Avg pipe ID | pipe material | Water Main Break Rates In the USA and Canada: A Comprehensive Study) | Water Main Break Rates In the USA and Canada: A Comprehensive Study) | We assume that the average pipe ID is similar to the average pipe ID for potable water.
Surface roughness | pipe material | Engineering Toolbox, Roughness & Surface Coefficients
Flow rate (normalized to ID) |  | Data gap
Leaks/distance | pipe material | We have data for water mains from Water Main Break Rates In the USA and Canada: A Comprehensive Study) . Apply to all pipe applications
water loss/leak/year | - | We have data for water mains from Water Main Break Rates In the USA and Canada: A Comprehensive Study) . Apply to all pipe applications
Material cost/length of pipe | pipe material | PVC vs Ductile Iron Pipe Installed Cost Comparison Calculator; A Framework to Evaluate the Life Cycle Costs and Environmental Impacts of Water Pipelines;PVC vs Ductile Iron Pipe Installed Cost Comparison Calculator; Currently have some estimates for PVC, DI. Need to estimate other materials. |  | Sources listed do not have all information on costs by pipe material; and the emphasis is on lead. PVC and DI pipes; Potentially use cost deltas (savings) between PVC relative to other materials; Vet with SMEs.
Manufacturing cost/length of pipe | pipe material | Wastewater Technology Fact Sheet Sewers, Force Main;
Transport cost /length of pipe | - | Life cycle assessment of PVC water and sewer pipe and comparative sustainability analysis of pipe materials;
Installation cost/length of pipe | - | What would it cost to replace all the nation’s lead water pipes? (Brookings); Deteriorating Buried Infrastructure Management Challenges and Strategies;
Pumping energy to compensate for leaks | - | Will come for pumps research
Embodied energy/length of pipe (Cradle to gate) | pipe material | Life Cycle Analysis for Water and Wastewater Pipe Materials
Embodied carbon/length of pipe (Cradle to gate) | pipe material | Life Cycle Analysis for Water and Wastewater Pipe Materials
Lifetime of pipe | pipe material | We have data for water mains from Water Main Break Rates In the USA and Canada: A Comprehensive Study) . Apply to all pipe applications
Avoided water contamination from water main breaks |  | Plan to use facts/stats from outsider resources. Not quantifying health impacts ourselves. |  | Secondary priority
Avoided contamination from corrosion (led)
Note on C35: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Rolled up "Right sizing" into ASD savings. We will give two values: one for right sizing and one for load matching

## Research -Water Infrastructure
Drinking Water and Wastewater Systems Research
This tab includes the research finding for drinking water and wastewater piping systems. The research findings on this tab are used as inputs in the 'Piping Calculation' tab.
EPRI: Electricity Use and Management in the Municipal Water Supply and Wastewater Industries
https://www.epri.com/research/products/000000003002001433
Groundwater systems typically have a different profile because the energy intensity for treatment is often negligible.
Active public drinking water systems in the US | 153000 | # of systems
Annual public drinking water system electricity consumption | 39.2 | Billion kWh
Percent pumping electricity consumption | 86%
https://www.epri.com/research/products/000000003002001433
While pumping does not have the same impact on overall energy performance as it does in drinking water treatment systems, it can often range from10% to 15% of overall energy use at the facility. By including the energy used by lift stations scattered throughout the collection area, the overall impact can be significant.
In contrast to drinking water systems where pumping accounts for most energy use, wastewater treatment is more closely related to treatment needs. Advanced wastewater treatment usually includes aeration for removing dissolved organic matter and nutrients; thus, aeration is the principal energy-using process in wastewater treatment.
Active public wastewater plants in the US | 15617 | # of systems
Annual public wastewater system energy consumption | 30.2 | Billion kWh
Percent pumping electricity consumption | 12% |  | Does not include energy used by lift station pumps, only facility pumping systems
https://www.epri.com/research/products/000000003002001433
EPRI: Water & Sustainability (Volume 4): U.S. Electricity Consumption for Water Supply & Treatment - The Next Half Century
https://www.epri.com/research/products/000000000001006787
Along with the approximately 16,000 publicly owned wastewater treatment plants in the United States, there are approximately 23,000 additional treatment facilities that are privately owned and operated, according to the United States Geological Survey (USGS). These are generally captive facilities associated with industrial plants and commercial operations.
The average size of privately owned wastewater treatment facilities will fall into the smallest size range of POTWs.
Given the smaller size and potentially higher loadings, the unit electricity consumption of these types of facilities will tend to be higher than for POTWs. A reasonable estimate of unit electricity consumption would be about 2,500 kWh/million gallons (0.661 kWh/cubic meter).
ASCE Drinking Water Report Card
https://infrastructurereportcard.org/wp-content/uploads/2017/01/Drinking-Water-2021.pdf
Water consumption per person | 82 | gal/day/person
Active drinking water systems in the US | 148000 | # of systems
length of drinking water piping | 2.2 | million miles
drinking water consumption per year | 14235 | billion gallons
Drinking water losses per year | 2190 | billion gallons
Estimated water pipes to be replaced in 2020 | 12000 | miles
Water Main Breaks per year | 250000 | breaks/year
There is a water main break every two minutes and an estimated 6 billion gallons of treated water lost each day in the U.S., enough to fill over 9,000 swimming pools.
About 39 billion gallons of water a day are withdrawn from surface water or groundwater sources for public supply. Public supply use represents about 12% of total freshwater withdrawals.
Our nation’s drinking water systems face staggering public investment needs over the next several decades. ASCE’s 2020 economic study, “The Economic Benefits of Investing in Water Infrastructure: How a Failure to Act Would Affect the U.S. Economic Recovery” found that the annual drinking water and wastewater investment gap will grow to $434 billion by 2029. Additionally, the cost to comply with the EPA’s 2019 Lead and Copper Rule is estimated at between $130 million and $286 million.
As the nation faces more frequent extreme weather events, water utilities are taking action to increase the resilience of their systems to ensure safety and reliability.
ASCE Wastewater Report Card
https://infrastructurereportcard.org/wp-content/uploads/2020/12/Wastewater-2021.pdf
Wastewater processed per day | 62.5 | billion gal/day
Active wastewater treatment plants in the US | 16000 | # of systems
Estimated water pipes replaced in 2019 | 4700 | miles
Cost to replace pipes replaced in 2019 | 3 | $ billion
length of municipal wastewater pipe | 800000 | miles
EPA: The Sources and Solutions: Wastewater
Source: https://www.epa.gov/nutrientpollution/sources-and-solutions-wastewater
16,000 publicly owned treatment works (POTWs) that treat domestic sewage and have a combined capacity of 150 billion gallons a day (bgd) (2017 estimate); USGS: 34 Bgal of wastewater/day, including domestic/industrial sewage and other wastewater (2015 estimate)
Daily Sewage/Wastewater processed | 34 | Bgal/day
Annual Sewage/Wastewater processed | 12410 | Bgal/day
EPA: Information about Public Water Systems
Source: https://www.epa.gov/dwreginfo/information-about-public-water-systems
There are over 148,000 public water systems in the United States.
A public water system provides water for human consumption through pipes or other constructed conveyances to at least 15 service connections or serves an average of at least 25 people for at least 60 days a year. A public water system may be publicly or privately owned.
Good Resource: https://www.epa.gov/dwreginfo/drinking-water-distribution-system-tools-and-resources
USGS: Estimated use of water in the United States in 2015
Source: https://pubs.er.usgs.gov/publication/cir1441
Public Supply Withdrawals (2015 estimate)* | 39 | Bgal/day
Annual Public Supply Withdrawals | 14235 | Bgal
*Incudes domestic, commercial, and industrial purposes. Part of the total is used for public services, such as public pools, parks, firefighting, water and wastewater treatment, and municipal buildings, and some is unaccounted for because of leaks, flushing, tower maintenance, and other system losses.
Dieter, C.A., Maupin, M.A., Caldwell, R.R., Harris, M.A., Ivahnenko, T.I., Lovelace, J.K., Barber, N.L., and Linsey, K.S., 2018, Estimated use of water in the United States in 2015: U.S. Geological Survey Circular 1441, 65 p., https://doi.org/10.3133/cir1441. [Supersedes USGS Open-File Report 2017–1131.]

## Stats
Constants, Conversions, and Statistics
This tab include all constants, conversions, and statistics used to determine the savings opportunities for plastic pipes and pumps. Details on calculation inputs are found on the 'Research' tab.
Constants Information
Information | Value | Units
National Electricity Cost (2022) | 0.0845 | $ per kWh (2022) | https://www.eia.gov/outlooks/steo/data/browser/#/?v=19
National Water Cost* | 0.009863 | $ per gallon | https://www.circleofblue.org/2010/world/the-price-of-water-a-comparison-of-water-rates-usage-in-30-u-s-cities/
Carbon Intensity | 0.00039 | metric tons per kWh | https://www.eia.gov/environment/emissions/carbon/#:~:text=Between%202005%20and%202021%2C%20the,to%200.39%20mt%20per%20megawatthour
*Assuming 30$/month @ 100 gal/day
Conversion Information
Equivalency Factors
1 metric ton of C02 | 0.223 | Gas power cars avoided annually |  | https://www.epa.gov/energy/greenhouse-gas-equivalencies-calculator#results
1 GWh of electricity | 94.0291 | American homes |  | https://www.eia.gov/tools/faqs/faq.php?id=97&t=3
Water Infrastructure
Drinking Water Infrastructure Information | Value | Units
Number of public water systems in the United States | 148000 | drinking water systems | ASCE Drinking Water Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2017/01/Drinking-Water-2021.pdf
| 153000 | drinking water systems | EPRI: Electricity Use and Management in the Municipal Water Supply and Wastewater Industries, https://www.epri.com/research/products/000000003002001433
| 207803 | drinking water systems | Utah State University, https://digitalcommons.usu.edu/cgi/viewcontent.cgi?article=1173&context=mae_facpub
Nationwide length of installed water mains | 2.2 | million mi | ASCE Drinking Water Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2017/01/Drinking-Water-2021.pdf
| 1.2 | million mi | Utah State University, https://digitalcommons.usu.edu/cgi/viewcontent.cgi?article=1173&context=mae_facpub
Estimated water mains to be replaced in 2020 | 12000 | miles | ASCE Drinking Water Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2017/01/Drinking-Water-2021.pdf
Nationwide consumption of drinking water | 14235 | billion gal/yr | USGS: Estimated use of water in the United States in 2015, https://pubs.er.usgs.gov/publication/cir1441
| 14235 | billion gal/yr | ASCE Drinking Water Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2017/01/Drinking-Water-2021.pdf
Nationwide drinking water leakage | 10% | % of total | Utah State University, https://digitalcommons.usu.edu/cgi/viewcontent.cgi?article=1173&context=mae_facpub
| 16% | % of total
Wastewater Infrastructure Information | Value | Units
Number of wastewater systems in the United States | 16000 | wastewater system | ASCE Wastewater Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2020/12/Wastewater-2021.pdf
Number of wastewater systems in the United States | 15617 | wastewater systems | EPRI: Electricity Use and Management in the Municipal Water Supply and Wastewater Industries, https://www.epri.com/research/products/000000003002001433
Nationwide length of wastewater pipes | 0.8 | million mi | ASCE Wastewater Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2020/12/Wastewater-2021.pdf
Estimated wastewater pipes replaced in 2019 | 4700 | miles | ASCE Wastewater Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2020/12/Wastewater-2021.pdf
Wastewater processed per year | 22812.5 | billion gal/yr | ASCE Wastewater Infrastructure Report Card, https://infrastructurereportcard.org/wp-content/uploads/2020/12/Wastewater-2021.pdf
| 12410 | billion gal/yr | EPA: The Sources and Solutions: Wastewater, https://www.epa.gov/nutrientpollution/sources-and-solutions-wastewater
The research team included multiple values for certain statistics to showcase variation between research sources. The most accurate source identified by SMEs is highlighted green